## Sheet1
Influent NO3 concentration | (mg NO3/L) | 150
Influent NO3 concentration | (mg NO3-N/L) | 33.8952
Target NO3 concentration | (mg NO3/L) | 0
Target NO3 concentration | (mg NO3-N/L) | 0
Water temperature | (°C) | 6
Filling grade MBBR AnoxKaldnes K5 | (%) | 30
Design flow MBBR | (m3/day) | 12 | → | Needed MBBR volume | (m3) | 4.4857
Design mass flow MBBR | (kg NO3/day) | 1.8 |  | Total volume AnoxKaldnes K5 | (m3) | 1.3457
Design mass flow MBBR | (kg NO3-N/day) | 0.40674 |  | Total surface area AnoxKaldnes K5 | (m2) | 1076.5791
|  |  |  | HRT | (h) | 8.9715
Design Volume MBBR | (m3) | 4.5 | → | Maximum mass flow MBBR | (kg NO3-N/day) | 0.40803
Total volume AnoxKaldnes K5 | (m3) | 1.35 |  | Maximum flow MBBR | (m3/day) | 12.0381
Total surface area AnoxKaldnes K5 | (m2) | 1080 |  | HRT | (h) | 8.9715
Maximum denitrification rate @ influent temperature | (g NO3-N/m2.day) | 0.37781
Maximum denitrification rate @ influent temperature | (g NO3-N/m3.day) | 302.2477
Carbon source demand (mass flow) | (kg COD/day) | 3.2539 |  | 3.2643
Carbo ST consuption per day | (L/day) | 2.1693 |  | 2.1762
Selenoid dosing pump setting | (%) | 18.08% |  | 18.13%
Carbo ST cost per day | (€/day) | 2.3455 |  | 2.353
| (€/m3) | 0.19546 |  | 0.19484
Minimal P concentration of influent | (mg PO4-P/L) | 0.029658
P concentration of influent | (mg PO4-P/L) | 0
P demand (mass flow) | (kg PO4-P/day) | 0.0003559
Carbo ST vessel volume | (L) | 20
mL of 75% H3PO4 addition to Carbo ST vessel | (mL) | 10.1788

## Sheet2
MM N | 14.01 | g/mol |  | Temp (°C) | DN rate (mg N/(m3.day))
MM NO3 | 62 | g/mol |  | 1 | 0.26687
MM P | 30.97 | g/mol |  | 2 | 0.28608
MM PO4 | 91.97 | g/mol |  | 3 | 0.30668
MM H3PO4 | 97.994 | g/mol |  | 4 | 0.32876
MM NH4NO3 | 80.043 | g/mol |  | 5 | 0.35243
COD Carbo ST | 1.1232 | kgO2/L |  | 6 | 0.37781
Density Carbo ST | 1.1 | kg/L |  | 7 | 0.40501
Price Carbo ST | 0.67 | €/kg |  | 8 | 0.43417
Density H3PO4 75% | 1.36 | kg/L |  | 9 | 0.46543
m% H3PO4 | 75 | % |  | 10 | 0.49894
Price H3PO4 75% | 2 | €/kg |  | 11 | 0.53487
max pump flow Carbo ST | 2 | L/h | type 0206 | 12 | 0.57338
max pump flow drainage water | 2 | m3/h |  | 13 | 0.61466
Denitrification rate @20°C | 1 | g NO3-N/m2.d |  | 14 | 0.65892
Denitrification rate @20°C | 800 | g NO3-N/m3.d |  | 15 | 0.70636
Specific surface AnoxKaldnes K5 | 800 | m2/m3 |  | 16 | 0.75722
θ= Arrhenius coëfficiënt | 1.072 |  |  | 17 | 0.81174
ratio COD/N | 8 | / |  | 18 | 0.87018
ratio P/N | 0.000875 | / |  | 19 | 0.93284
COD Carbo ST | 1.5 | kgO2/L |  | 20 | 1
Density Carbo ST | 1.25 | kg/L |  | 21 | 1.072
Price Carbo ST | 0.865 | €/kg |  | 22 | 1.1492
|  |  |  | 23 | 1.2319
|  |  |  | 24 | 1.3206
|  |  |  | 25 | 1.4157